## Supporting Information
Techno-economic feasibility assessment of CO2 capture
from coal-fired power plants using molecularly imprinted polymer
Dawid P. Hanak*, Vasilije Manovic
Combustion and CCS Centre, Cranfield University,
Bedford, Bedfordshire, MK43 0AL, UK
Dataset
Corresponding author: *Dawid P. Hanak, d.p.hanak@cranfield.ac.uk
Hanak, D.P. and Manovic, V. (2018), "Techno-economic feasibility assessment of CO2 capture from coal-fired power plants using molecularly imprinted polymer", Fuel, 214, 512-520, doi: 10.1016/j.fuel.2017.10.107

## Performance
Case |  | Reference CFPP | MIPS C020 | MIPS C040 | MIPS C060 | MIPS C080 | MIPS C100 | MIPS C056 (REF) P=0% | MIPS C056 (REF) P=0.1% | MIPS C056 (REF) P=0.2% | MIPS C056 (REF) P=0.3% | MIPS C056 (REF) P=0.4% | MIPS C056 (REF) P=0.5% | MIPS C056 (REF) P=1.0% | MIPS C056 (REF) P=1.5%
Parameter | Unit |  | 0.2 | 0.4 | 0.6 | 0.8 | 1 | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 1 | 1.5
Fuel higher heating value | kJ/kg | 27013.898 | 27013.898 | 27013.898 | 27013.898 | 27013.898 | 27013.898 | 27013.898 | 27013.898 | 27013.898 | 27013.898 | 27013.898 | 27013.898 | 27013.898 | 27013.898
Fuel consumption | kg/s | 53.773 | 53.773 | 53.773 | 53.773 | 53.773 | 53.773 | 53.773 | 53.773 | 53.773 | 53.773 | 53.773 | 53.773 | 53.773 | 53.773
Heat transferred to the working medium in the boiler | MW | 1237.4721 | 1237.5641 | 1237.5641 | 1237.5641 | 1237.5641 | 1237.5641 | 1237.5641 | 1237.5641 | 1237.5641 | 1237.5641 | 1237.5641 | 1237.5641 | 1237.5641 | 1237.5641
Chemical energy carried with the fuel | MW | 1452.6183 | 1452.6183 | 1452.6183 | 1452.6183 | 1452.6183 | 1452.6183 | 1452.6183 | 1452.6183 | 1452.6183 | 1452.6183 | 1452.6183 | 1452.6183 | 1452.6183 | 1452.6183
Boiler efficiency | % | 85.1891 | 85.1954 | 85.1954 | 85.1954 | 85.1954 | 85.1954 | 85.1954 | 85.1954 | 85.1954 | 85.1954 | 85.1954 | 85.1954 | 85.1954 | 85.1954
CW Rate |  |  | 4770.6712 | 8647.4289 | 9947.0905 | 10613.9612 | 11019.3988 | 9756.4835 | 9756.2978 | 9754.8088 | 9753.8893 | 9752.9702 | 9752.5109 | 9748.4893 | 9745.7426
CFPP auxiliary electricity requirement
Coal Handlin and Conveying | MWel | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44
Pulverizers | MWel | 2.8971 | 2.8971 | 2.8971 | 2.8971 | 2.8971 | 2.8971 | 2.8971 | 2.8971 | 2.8971 | 2.8971 | 2.8971 | 2.8971 | 2.8971 | 2.8971
Sorbent Handling and Reagent preparation | MWel | 0.89 | 0.89 | 0.89 | 0.89 | 0.89 | 0.89 | 0.89 | 0.89 | 0.89 | 0.89 | 0.89 | 0.89 | 0.89 | 0.89
Ash handling | MWel | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53
Primary Air Fans | MWel | 1.3052 | 1.3052 | 1.3052 | 1.3052 | 1.3052 | 1.3052 | 1.3052 | 1.3052 | 1.3052 | 1.3052 | 1.3052 | 1.3052 | 1.3052 | 1.3052
Forced Draft Fans | MWel | 1.681 | 1.6809 | 1.6809 | 1.681 | 1.681 | 1.681 | 1.681 | 1.6809 | 1.681 | 1.681 | 1.681 | 1.681 | 1.681 | 1.681
Induced Draft Fans | MWel | 7.4582 | 7.4581 | 7.4581 | 7.4582 | 7.4583 | 7.4583 | 7.4582 | 7.4582 | 7.4582 | 7.4582 | 7.4582 | 7.4582 | 7.4582 | 7.4582
Wet FGD | MWel | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97
Miscellaneous balance of plant | MWel | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Steam turbine auxiliaries | MWel | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Condensate pumps | MWel | 0.76393 | 0.67983 | 0.70988 | 0.72651 | 0.73308 | 0.73783 | 0.72439 | 0.72442 | 0.72439 | 0.72439 | 0.72439 | 0.72439 | 0.72435 | 0.72434
Circulating water pumps | MWel | 1.6632 | 0.5675 | 1.0287 | 1.1833 | 1.2626 | 1.3108 | 1.1606 | 1.1606 | 1.1604 | 1.1603 | 1.1602 | 1.1601 | 1.1597 | 1.1593
Ground water pumps | MWel | 0.48 | 0.16386 | 0.29701 | 0.34165 | 0.36456 | 0.37848 | 0.33511 | 0.3351 | 0.33505 | 0.33502 | 0.33499 | 0.33497 | 0.33483 | 0.33474
Cooling tower fans | MWel | 2.44 | 0.83295 | 1.5098 | 1.7367 | 1.8532 | 1.924 | 1.7035 | 1.7034 | 1.7032 | 1.703 | 1.7028 | 1.7028 | 1.7021 | 1.7016
Transformer losses | MWel | 1.82 | 1.82 | 1.82 | 1.82 | 1.82 | 1.82 | 1.82 | 1.82 | 1.82 | 1.82 | 1.82 | 1.82 | 1.82 | 1.82
MIP PCC Auxiliary cosumption
FG Booster | MWel | 0 | 1.3772 | 1.3772 | 1.3772 | 1.3772 | 1.3772 | 1.3772 | 1.3772 | 1.3772 | 1.3772 | 1.3772 | 1.3772 | 1.3772 | 1.3772
WTPumps | MWel |  | 0.013697 | 0.013697 | 0.013697 | 0.01356 | 0.013697 | 0.013697 | 0.013697 | 0.013697 | 0.013697 | 0.013697 | 0.013697 | 0.013697 | 0.013697
Cooling air fan | MWel |  | 17.5637 | 8.7819 | 4.3909 | 4.3909 | 3.5127 | 6.2728 | 6.2728 | 6.2728 | 6.2728 | 6.2728 | 6.2728 | 6.2728 | 6.2728
CO2 pump | MWel |  | 0.59752 | 0.59757 | 0.59756 | 0.59757 | 0.59753 | 0.59757 | 0.59758 | 0.59758 | 0.59758 | 0.59758 | 0.59758 | 0.59758 | 0.59758
CO2 compressor | MWel |  | 36.2 | 36.2029 | 36.2026 | 36.2028 | 36.1935 | 36.2032 | 36.2038 | 36.2038 | 36.2038 | 36.2038 | 36.2038 | 36.2038 | 36.2038
System performance indicators
Gross electricity production | MWel | 580.4092 | 502.7485 | 535.4635 | 547.2131 | 552.7229 | 556.4291 | 545.5481 | 545.5481 | 545.5481 | 545.5481 | 545.5481 | 545.5481 | 545.5481 | 545.5481
Total auxiliary electricity consumption | MWel | 27.7386 | 80.3877 | 72.9101 | 68.9616 | 69.187 | 68.4373 | 70.7795 | 70.7799 | 70.7794 | 70.7791 | 70.7788 | 70.7787 | 70.7773 | 70.7764
Net electricity production | MWel | 552.6706 | 422.3608 | 462.5534 | 478.2515 | 483.5359 | 487.9918 | 474.7687 | 474.7682 | 474.7687 | 474.769 | 474.7693 | 474.7695 | 474.7708 | 474.7717
System performance indicators
Gross electric efficiency | %(HHV) | 39.9561 | 34.6098 | 36.862 | 37.6708 | 38.0501 | 38.3053 | 37.5562 | 37.5562 | 37.5562 | 37.5562 | 37.5562 | 37.5562 | 37.5562 | 37.5562
Net electric efficiency | %(HHV) | 38 | 29.1 | 31.8 | 32.9 | 33.3 | 33.6 | 32.7 | 32.7 | 32.7 | 32.7 | 32.7 | 32.7 | 32.7 | 32.7
Efficiency penalty | %pt | - | 8.9 | 6.2 | 5.1 | 4.7 | 4.4 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3
Fuel chemical energy consumption per unit gross electricity production | kWth/kWel | 2.5027 | 2.8894 | 2.7128 | 2.6546 | 2.6281 | 2.6106 | 2.6627 | 2.6627 | 2.6627 | 2.6627 | 2.6627 | 2.6627 | 2.6627 | 2.6627
Fuel chemical energy consumption per unit net electricity production | kWth/kWel | 2.6284 | 3.4393 | 3.1404 | 3.0374 | 3.0042 | 2.9767 | 3.0596 | 3.0596 | 3.0596 | 3.0596 | 3.0596 | 3.0596 | 3.0596 | 3.0596
Coal consumption per unit net electricity production | g/kWh | 350.2679 | 458.3351 | 418.5091 | 404.7719 | 400.3483 | 396.6928 | 407.7413 | 407.7417 | 407.7413 | 407.741 | 407.7408 | 407.7406 | 407.7395 | 407.7387
Environmental performance indictors
CO2 emission rate | kg/s | 121.641 | 12.1641 | 12.1641 | 12.1641 | 12.1641 | 12.1641 | 12.1641 | 12.1641 | 12.1641 | 12.1641 | 12.1641 | 12.1641 | 12.1641 | 12.1641
| kg/h | 437907.6 | 43790.76 | 43790.76 | 43790.76 | 43790.76 | 43790.76 | 43790.76 | 43790.76 | 43790.76 | 43790.76 | 43790.76 | 43790.76 | 43790.76 | 43790.76
| g/h | 437907600 | 43790760 | 43790760 | 43790760 | 43790760 | 43790760 | 43790760 | 43790760 | 43790760 | 43790760 | 43790760 | 43790760 | 43790760 | 43790760
CO2 mass fraction in the flue gas | wt% | 21.3173 | 21.3173 | 21.3173 | 21.3173 | 21.3173 | 21.3173 | 21.3173 | 21.3173 | 21.3173 | 21.3173 | 21.3173 | 21.3173 | 21.3173 | 21.3173
CO2 volume fraction in the flue gas | vol% | 14.178 | 14.178 | 14.178 | 14.178 | 14.178 | 14.178 | 14.178 | 14.178 | 14.178 | 14.178 | 14.178 | 14.178 | 14.178 | 14.178
CO2 intensity factor | g/kWh | 792.3482 | 103.6809 | 94.6718 | 91.5643 | 90.5636 | 89.7367 | 92.236 | 92.2361 | 92.236 | 92.2359 | 92.2359 | 92.2358 | 92.2356 | 92.2354
Cost of electricity | £/MWh | 36.9 | 71.5555 | 60.5104 | 56.9345 | 55.805 | 54.96 | 57.4983 | 62.3069 | 67.1155 | 71.9241 | 76.7328 | 81.5413 | 105.5844 | 129.6274
Cost of CO₂ avoided | £/t | - | 50.0629 | 33.6919 | 28.4736 | 26.8341 | 25.6078 | 29.3009 | 36.1251 | 42.9493 | 49.7735 | 56.5978 | 63.422 | 97.5432 | 131.6643
Gross power output distribution |  | Reference CFPP | MIPS C020 | MIPS C040 | MIPS C060 | MIPS C080 | MIPS C100 | MIPS C056 (REF) P=0% | MIPS C056 (REF) P=0.1% | MIPS C056 (REF) P=0.2% | MIPS C056 (REF) P=0.3% | MIPS C056 (REF) P=0.4% | MIPS C056 (REF) P=0.5% | MIPS C056 (REF) P=1.0% | MIPS C056 (REF) P=1.5%
Gross power plant output |  | 580.4092 | 502.7485 | 535.4635 | 547.2131 | 552.7229 | 556.4291 | 545.5481 | 545.5481 | 545.5481 | 545.5481 | 545.5481 | 545.5481 | 545.5481 | 545.5481
Steam extraction |  | 0 | 77.6607 | 44.9458 | 33.1961 | 27.6863 | 23.9801 | 34.8611 | 34.8611 | 34.8611 | 34.8611 | 34.8611 | 34.8611 | 34.8611 | 34.8611
Power plant auxiliaries |  | 27.7386 | 24.6355 | 25.9368 | 26.3796 | 26.6049 | 26.7427 | 26.315 | 26.3149 | 26.3144 | 26.3141 | 26.3138 | 26.3137 | 26.3123 | 26.3114
CO2 compression |  | 0 | 36.7976 | 36.8005 | 36.8002 | 36.8003 | 36.791 | 36.8008 | 36.8013 | 36.8013 | 36.8013 | 36.8013 | 36.8013 | 36.8013 | 36.8013
Pumps and fans |  | 0 | 18.9546 | 10.1728 | 5.7818 | 5.7817 | 4.9037 | 7.6637 | 7.6637 | 7.6637 | 7.6637 | 7.6637 | 7.6637 | 7.6637 | 7.6637
Net power plant output |  | 552.6706 | 422.3608 | 462.5534 | 478.2515 | 483.5359 | 487.9918 | 474.7687 | 474.7682 | 474.7687 | 474.769 | 474.7693 | 474.7695 | 474.7708 | 474.7717
Parasitic load |  | 27.7386 | 158.0484 | 117.8558 | 102.1577 | 96.8733 | 92.4175 | 105.6405 | 105.641 | 105.6405 | 105.6402 | 105.6399 | 105.6398 | 105.6384 | 105.6375
Check Sum |  | 580.4092 | 580.4092 | 580.4092 | 580.4092 | 580.4092 | 580.4092 | 580.4092 | 580.4092 | 580.4092 | 580.4092 | 580.4092 | 580.4092 | 580.4092 | 580.4092
Parasitic load distribution |  | MIPS C056 (REF) P=0%
Steam extraction |  | 33%
Power plant auxiliaries |  | 24.91%
CO₂ compression unit |  | 34.84%
Pumps and fans |  | 7.254%
Sensitivity analysis
Capacity | mmolCO2/g | 0.2 | 0.4 | 0.6 | 0.8 | 1
Material cost | £/t | 10 | 10 | 10 | 10 | 10
Cost of electricity | £/MWh | 71.3099 | 60.2862 | 56.7176 | 55.5905 | 54.7475
Cost of CO2 avoided | £/t | 49.7087 | 33.3726 | 28.1661 | 26.5304 | 25.3072
Capacity | mmolCO2/g | 0.2 | 0.4 | 0.6 | 0.8 | 1
Material cost (£/tonne) | £/t | 50 | 50 | 50 | 50 | 50
Cost of electricity (£/MWh) | £/MWh | 71.419 | 60.3858 | 56.814 | 55.6858 | 54.8419
Cost of CO2 avoided (£/t) | £/t | 49.8661 | 33.5145 | 28.3027 | 26.6654 | 25.4408
Capacity | mmolCO2/g | 0.2 | 0.4 | 0.6 | 0.8 | 1
Material cost (£/tonne) | £/t | 100 | 100 | 100 | 100 | 100
Cost of electricity (£/MWh) | £/MWh | 71.5555 | 60.5104 | 56.9345 | 55.805 | 54.96
Cost of CO2 avoided (£/t) | £/t | 50.0629 | 33.6919 | 28.4736 | 26.8341 | 25.6078
Capacity | mmolCO2/g | 0.2 | 0.4 | 0.6 | 0.8 | 1
Material cost (£/tonne) | £/t | 500 | 500 | 500 | 500 | 500
Cost of electricity (£/MWh) | £/MWh | 72.6469 | 61.5069 | 57.8983 | 56.7583 | 55.9046
Cost of CO2 avoided (£/t) | £/t | 51.6374 | 35.1111 | 29.8401 | 28.1838 | 26.9436
Capacity | mmolCO2/g | 0.2 | 0.4 | 0.6 | 0.8 | 1
Material cost (£/tonne) | £/t | 1000 | 1000 | 1000 | 1000 | 1000
Cost of electricity (£/MWh) | £/MWh | 74.0111 | 62.7527 | 59.1032 | 57.9499 | 57.0854
Cost of CO2 avoided (£/t) | £/t | 53.6054 | 36.8851 | 31.5484 | 29.871 | 28.6134
Capacity | mmolCO2/g | 0.2 | 0.4 | 0.6 | 0.8 | 1
Material cost (£/tonne) | £/t | 1000 | 1000 | 1000 | 1000 | 1000
Cost of electricity (£/MWh) | £/MWh | 78.1036 | 66.4899 | 62.7176 | 61.5249 | 60.6277
Cost of CO2 avoided (£/t) | £/t | 59.5092 | 42.2073 | 36.673 | 34.9324 | 33.6228
Capacity | mmolCO2/g | 0.2 | 0.4 | 0.6 | 0.8 | 1
Material cost (£/tonne) | £/t | 5000 | 5000 | 5000 | 5000 | 5000
Cost of electricity (£/MWh) | £/MWh | 84.9251 | 72.7183 | 68.7417 | 67.4832 | 66.5316
Cost of CO2 avoided (£/t) | £/t | 69.3498 | 51.0771 | 45.2141 | 43.3682 | 41.9718
Cost of CO₂ avoided (MIP=10 £/t)
Cost of CO₂ avoided (MIP=50 £/t)
Cost of CO₂ avoided (MIP=100 £/t)
Cost of CO₂ avoided (MIP=500 £/t)
Cost of CO₂ avoided (MIP=1000 £/t)
Cost of CO₂ avoided (MIP=2500 £/t)
Cost of CO₂ avoided (MIP=5000 £/t)

## Comparison
| Efficiency penalty |  |  | Cost of CO2 avoided
| Minimum | Maximum | Difference | Minimum | Maximum | Difference
Adsorption using MIPs | 4.4 | 8.9 | 4.5 | 29.3 | 131 | 101.7
Calcium looping | 3 | 8 | 5 | 7 | 87.5 | 80.5
Chemical solvent scrubbing | 7 | 13 | 6 | 30 | 75 | 45