## Dataset
Advanced power cycles for coal-fired power plants based on calcium looping combustion:
A techno-economic feasibility assessment
Sebastian S. Michalski, Dawid P. Hanak*, Vasilije Manovic
Energy and Power, School of Water, Energy and Environment, Cranfield University,
Bedford, Bedfordshire, MK43 0AL, UK
Dataset
Corresponding author: *Dawid P. Hanak, d.p.hanak@cranfield.ac.uk

## Table 1
Case
|  | Summary Table | OPT
Parameter, Unit |  |  | Case
|  |  | s-CO2 R-C2E2 | Xe | s-CO2 P1E1 | He | N2 | s-CO2 R-C2E2/R-C2E1 | s-CO2 R-C2E2/PE2 | s-CO2 R-C2E2/PE1 | REF
Assumptions |  | CO2 live tempertaure, °C | 665 | 710 | 670 | 665 | 665 | 665 | 665 | 665
|  | Main compressor outlet pressure, Mpa | 30 | 32 | 32 | 7 | 25 | 30 | 30 | 30 | [5 empty] | 1.1772 |  | 1556.695 |  |  | 1200
|  | Temperature difference - cold end of REC1 | 5 | 5 | 5 | 7.5 | 5 | 7.5 | 7.5 | 7.5
|  | Temperature difference - cold end of REC2 | 5 | - | - | - | - | 5 | 5 | 5
|  | Temperature difference - hot end of REC2 | 5 | - | - | 15 | 15 | 5 | 5 | 5
|  | Bottomming cycle compressor outlet pressure, Mpa | - | - | - | 12 | 30 | 30 | 40 | 35 | [7 empty] | 1297245.8272 | 1297.2458
|  | Temperature difference - cold end of REC3 | - | - | - | - | - | 15 | 15 | 15
|  | Temperature difference - hot end of REC3 | - | - | - | - | - | - | 15 | 15
|  | Temperature difference - cold end of REC4 | - | - | - | - | - | 5 | - | -
|  | Temperature difference - hot end of REC4 | - | - | - | - | - | 15 | - | -
Thermodynamic results | Auxiliary power requirement, MW | of CCT | 44.983 | 44.9895 | 44.9895 | 44.9895 | 44.9895 | 44.9833 | 44.9833 | 44.9833
|  | of CaLC | 18.288 | 18.2924 | 18.2924 | 18.2924 | 18.2924 | 18.288 | 18.288 | 18.288 | [12 empty] | 10462.5 |  | 10.4625
|  | of s-CO2 cycle | 6.9534 | 70.3377 | 6.8635 | 6.8537 | 6.8361 | 6.1233 | 5.9594 | 6.3274
|  | Total | 70.2244 | 133.6197 | 70.1455 | 70.1357 | 70.118 | 69.3947 | 69.2307 | 69.5987
|  | Gross power - main cycle | 640.582 | 649.0019 | 614.0209 | 500.9923 | 480.1677 | 550.2294 | 550.2294 | 550.2294
|  |  | - | - | - | 47.706 | 38.1008 | 45.2156 | 32.2723 | 50.8739
|  | Net power, MW | 565.6386 | 515.3822 | 543.8754 | 478.5627 | 448.1505 | 526.0503 | 513.2709 | 531.5045
|  | Net efficiency, % | 38.9414 | 35.4815 | 37.4431 | 32.9467 | 30.8529 | 36.216 | 35.3362 | 36.5915 | [9 empty] | 1200 |  | 1323899891.476 | 1103249.9096 | 105.448 | 1103.2499
|  | Specific CO2 emission, kg/MWh | 91.5307 | 100.502 | 95.2368 | 108.2344 | 115.5793 | 98.414 | 100.8643 | 97.4041 | 796.8 | [8 empty] | 2000 |  |  | 661949.9457 | 63.2688
Economic results | Investment cost, M€ | of CCT | 22.6105 | 22.6134 | 22.6134 | 22.6134 | 22.6134 | 22.6115 | 22.6115 | 22.6115
|  | of CaLC | 395.5945 | 394.0377 | 392.1821 | 381.6307 | 377.1607 | 379.74 | 377.6746 | 383.8563
|  | of s-CO2 cycle | 164.6773 | 107.4427 | 123.5623 | 158.7178 | 159.4795 | 157.5247 | 146.7388 | 159.4594
|  | Total as-spent investment cost, M€ | 1447.0982 | 1323.8999 | 1353.792 | 1405.3527 | 1397.5815 | 1398.8864 | 1371.955 | 1411.567
|  |  | 2558.3444 | 2568.773 | 2489.1583 | 2936.6116 | 3118.5537 | 2659.2254 | 2672.9645 | 2655.7948
|  | Break-even electricity price, €/MWh | 71.1465 | 75.0327 | 71.7361 | 82.7877 | 88.0696 | 75.2155 | 76.3806 | 74.7644 | 59.63 |  | 3.8862 | 0.58963 | 11.6413
|  | CO2 Avoided cost | 16.3292 | 22.1209 | 17.2559 | 33.6319 | 41.748 | 22.3164 | 24.0691 | 21.6393
11.5165
|  | Summary Table | NOM |  |  |  |  | 0.3755 |  |  | 1.1931
0.45106
Parameter, Unit |  |  | Case
|  |  | s-CO2 R-C2E2 | Xe | s-CO2 P1E1 | He | N2 | s-CO2 R-C2E2/R-C2E1 | s-CO2 R-C2E2/PE2 | s-CO2 R-C2E2/PE1
Thermodynamic results | Auxiliary power requirement, MW | of CCT | 44.9933 | 44.9917 | 44.9917 | 44.9917 | 44.9917 | 44.9933 | 44.9933 | 44.9933
|  | of CaLC | 18.8894 | 18.8868 | 18.8868 | 18.8868 | 18.8868 | 18.8894 | 18.8894 | 18.8894
|  | of s-CO2 cycle | 7.629 | 77.7737 | 7.2513 | 7.2601 | 6.9123 | 6.6103 | 6.4897 | 6.8738
|  | Total | 71.5118 | 141.6521 | 71.1297 | 71.1386 | 70.7907 | 70.493 | 70.3724 | 70.7565 |  | 70.5224
|  | Gross power - Main cycle | 584.0505 | 598.2037 | 581.4933 | 471.0855 | 450.7129 | 501.6478 | 501.6478 | 501.6478
|  | Gross power - bottoming cycle | - | - | - | 33.0863 | 27.7172 | 35.2943 | 27.9365 | 48.127
|  | Net power, MW | 507.9119 | 456.5516 | 510.3635 | 433.0332 | 407.6394 | 466.4491 | 459.2119 | 479.0183 |  | 53.8119 | -23.5184 |  |  | -53.8119 | 23.5184 |  | -9.7073
|  | Net efficiency, % | 34.9672 | 31.4313 | 35.136 | 29.8122 | 28.064 | 32.1127 | 31.6145 | 32.978 | [5 empty] | -10.5438 | 5.4311
|  | Specific CO2 emission, kg/MWh | 101.9807 | 113.3716 | 101.4179 | 119.5289 | 126.9749 | 111.0458 | 112.7959 | 108.132
Economic results | Investment cost, M€ | of CCT | 22.6151 | 22.6143 | 22.6143 | 22.6143 | 22.6143 | 22.616 | 22.616 | 22.616
|  | of CaLC | 395.7982 | 394.1018 | 392.1257 | 384.3946 | 377.6679 | 380.2856 | 378.1931 | 384.4141
|  | of s-CO2 cycle | 150.0862 | 106.6678 | 121.0045 | 170.3976 | 172.8836 | 144.1333 | 139.537 | 151.8011
|  | Total as-spent investment cost, M€ | 1416.9573 | 1322.4124 | 1348.3155 | 1435.6232 | 1426.7363 | 1371.9757 | 1357.9586 | 1396.6962
|  |  | 2789.7701 | 2896.5235 | 2641.8728 | 3315.2727 | 3499.9959 | 2941.3188 | 2957.15 | 2915.7471
|  | Break-even electricity price, €/MWh | 78.3522 | 84.5155 | 76.2215 | 92.2274 | 97.6167 | 83.952 | 84.8619 | 82.4475 |  | 2.1308 | 8.294 | 0 | 16.006 | 21.3952 | 7.7306 | 8.6404
|  |  | -3.9742 | -4.0502 | -2.3071 | -3.1345 | -2.789 | -4.1032 | -3.7217 | -3.6134
|  |  | 7.2057 |  | 4.4853 | 9.4397
|  |  |  | 23.5184 | 48.9122 | -9.8976
|  |  |  | 0.054311 | 0.11999 | -0.021219
[8 empty] | 1200 |  | kg
[8 empty] | 1200000 |  | t
1102.0103
|  |  | 3.9742 | 4.0502 | 2.3071 | 3.1345 | 2.789 | 4.1032 | 3.7217 | 3.6134
|  |  | 7.2057 | 9.4827 | 4.4853 | 9.4397 | 9.547 | 8.7366 | 8.4813 | 7.6831

## CaLC PS
|  |  | Fig 6 | Fig 7
Molar oxygen content in flue gas |  | % | 3.5% | 3% | 2.5% | 2% | 1.5% | 1% | 2% | 2% | 2% | 2% | 2%
Percentage of sorbent make up |  | % | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 4% | 5% | 6% | 7%
Net efficiency | s-CO2 RC2E2 | % | 34.6995 | 34.7923 | 34.8873 | 34.973 | 35.0489 | 35.1286 | 34.9672 | 34.3526 | 33.7271 | 33.1569 | 32.6235 | 0.3363 | 2.3437 | 6.9692
| Xenon | % | 31.3007 | 31.3482 | 31.3936 | 31.437 | 31.4776 | 31.5084 | 31.4313 | 30.8684 | 30.3102 | 29.8004 | 29.3085 | 0.16014 | 2.1228 | 13.2561
| s-CO2 PE2 | % | 34.8567 | 34.9269 | 34.9962 | 35.0634 | 35.1257 | 35.1769 | 35.136 | 34.4443 | 33.8342 | 33.2772 | 32.7397 | 0.25002 | 2.3963 | 9.5846
| Helium | % | 29.3076 | 29.4854 | 29.6557 | 29.8176 | 29.9718 | 30.1077 | 29.8122 | 29.2243 | 28.6401 | 28.1068 | 27.5923 | 0.6223 | 2.2199 | 3.5673
| Nitrogen | % | 27.4659 | 27.6765 | 27.8777 | 28.0689 | 28.2499 | 28.4134 | 28.064 | 27.4853 | 26.9119 | 26.3863 | 25.8811 | 0.73691 | 2.1829 | 2.9622
| s-CO2 RC2E2/RC2E1 | % | 31.5474 | 31.7456 | 31.9384 | 32.1199 | 32.2943 | 32.458 | 32.1127 | 31.4843 | 30.8631 | 30.2875 | 29.7661 | 0.71242 | 2.3466 | 3.2939
Break-even price of electricity | s-CO2 RC2E2 | EUR/MWh | 78.933 | 78.7177 | 78.5007 | 78.3055 | 78.1317 | 77.9579 | 78.3522 | 82.3302 | 86.2378 | 90.0317 | 93.7157 | 0.75982 | 15.3635 | 20.22
| Xenon | EUR/MWh | 84.8375 | 84.7102 | 84.5923 | 84.4775 | 84.3708 | 84.3279 | 84.5155 | 88.9857 | 93.2943 | 97.43 | 101.5952
| s-CO2 PE2 | EUR/MWh | 76.7721 | 76.6246 | 76.4761 | 76.3311 | 76.1977 | 76.1224 | 76.2215 | 80.3395 | 84.1702 | 87.8445 | 91.5429 | 0.50214 | 15.3215 | 30.5125
| Helium | EUR/MWh | 93.6364 | 93.1247 | 92.643 | 92.1873 | 91.7574 | 91.4231 | 92.2274 | 97.1302 | 101.8874 | 106.4676 | 111.095 | 1.7016 | 18.8676 | 11.0881
| Nitrogen | EUR/MWh | 99.4522 | 98.7862 | 98.1622 | 97.5744 | 97.025 | 96.5787 | 97.6167 | 102.9075 | 108.05 | 113.0166 | 118.0353 | 2.2075 | 20.4186 | 9.2497
| s-CO2 RC2E2/RC2E1 | EUR/MWh | 85.2434 | 84.7719 | 84.3193 | 83.8975 | 83.4964 | 83.1264 | 83.952 | 88.4277 | 92.7995 | 97.0815 | 101.1997 | 1.6455 | 17.2476 | 10.4817
|  |  | 0.3363 |  | 6.9692 |  |  |  | 2.3437
|  |  | -0.75982 |  | 20.22 |  |  |  | -15.3635
Fig 5
Fig 6

## R-C2E2 + Xe + PE2
S-CO2 RC2E2 | Live temperature | deg C | 500 | 500 | 500 | 500 | 500 | 550 | 550 | 550 | 550 | 550 | 600 | 600 | 600 | 600 | 600 | 650 | 650 | 650 | 650 | 650 | 660 | 660 | 660 | 660 | 660
| Live pressure | Mpa | 18 | 21 | 24 | 27 | 30 | 30 | 27 | 24 | 21 | 18 | 18 | 21 | 24 | 27 | 30 | 30 | 27 | 24 | 21 | 18 | 18 | 21 | 24 | 27 | 30
| Net efficiency | % | 30.7071 | 31.7617 | 32.3883 | 32.7629 | 32.9791 | 34.9361 | 34.6826 | 34.2684 | 33.6094 | 32.5161 | 34.1635 | 35.2822 | 35.9698 | 36.4103 | 36.689 | 38.2637 | 37.9667 | 37.5119 | 36.8049 | 35.6721 | 35.9629 | 37.1033 | 37.8018 | 38.2619 | 38.5563
| Break-even price of electricity | EUR/MWh | 88.9132 | 86.1921 | 84.777 | 84.0507 | 83.733 | 79.0399 | 79.4074 | 80.1491 | 81.5007 | 84.0374 | 80.0668 | 77.6998 | 76.4028 | 75.668 | 75.2767 | 72.2216 | 72.6183 | 73.3302 | 74.5691 | 76.784 | 76.1891 | 74.0034 | 72.7834 | 72.074 | 71.6843
Xe | Live temperature | deg C | 500 | 500 | 500 | 500 | 500 | 550 | 550 | 550 | 550 | 550 | 600 | 600 | 600 | 600 | 600 | 650 | 650 | 650 | 650 | 650 | 700 | 700 | 700 | 700 | 700
| Live pressure | Mpa | 28 | 31 | 34 | 37 | 40 | 40 | 37 | 34 | 31 | 28 | 28 | 31 | 34 | 37 | 40 | 40 | 37 | 34 | 31 | 28 | 28 | 31 | 34 | 37 | 40
| Net efficiency | % | 27.0922 | 27.0627 | 26.902 | 26.6455 | 26.3166 | 28.7723 | 29.05 | 29.2542 | 29.3607 | 29.333 | 31.3617 | 31.434 | 31.3721 | 31.2112 | 30.9754 | 32.9677 | 33.1686 | 33.2943 | 33.3205 | 33.2116 | 34.9089 | 35.0467 | 35.0498 | 34.9534 | 34.7813
| Break-even price of electricity | EUR/MWh | 97.8693 | 98.1269 | 98.8445 | 99.9113 | 101.26 | 92.6839 | 91.7007 | 90.9518 | 90.4991 | 90.445 | 84.6384 | 84.5727 | 84.8547 | 85.3961 | 86.1405 | 80.9778 | 80.3971 | 79.9952 | 79.8246 | 79.9664 | 76.1233 | 75.9359 | 76.0311 | 76.335 | 76.8004
s-CO2 PE2 | Live temperature | deg C | 500 | 500 | 500 | 500 | 500 | 550 | 550 | 550 | 550 | 550 | 600 | 600 | 600 | 600 | 600 | 650 | 650 | 650 | 650 | 650 | 665 | 665 | 665 | 665 | 665
| Live pressure | Mpa | 28 | 31 | 34 | 37 | 40 | 40 | 37 | 34 | 31 | 28 | 28 | 31 | 34 | 37 | 40 | 40 | 37 | 34 | 31 | 28 | 28 | 31 | 34 | 37 | 40
| Net efficiency | % | 31.2987 | 31.3579 | 31.2568 | 31.0946 | 30.8548 | 32.9241 | 33.134 | 33.271 | 33.3296 | 33.2621 | 34.9757 | 35.114 | 35.0821 | 34.9495 | 34.7944 | 36.4861 | 36.6329 | 36.7027 | 36.6843 | 36.57 | 37.0099 | 37.2194 | 37.2167 | 37.1376 | 37.0032
| Break-even price of electricity | EUR/MWh | 85.2576 | 85.2971 | 85.7583 | 86.3893 | 87.2361 | 81.7934 | 81.1212 | 80.6275 | 80.3231 | 80.3147 | 76.4637 | 76.3199 | 76.5432 | 76.9637 | 77.4504 | 73.9329 | 73.5098 | 73.2373 | 73.1391 | 73.2321 | 72.3948 | 72.1315 | 72.265 | 72.5447 | 72.9341
Fig. 7.

## He + N2 + RC2E2-RC2E1
He | Live temperature | deg C | 500 | 500 | 500 | 500 | 500 | 550 | 550 | 550 | 550 | 550 | 600 | 600 | 600 | 600 | 600 | 650 | 650 | 650 | 650 | 650 | 665 | 665 | 665 | 665 | 665
| Live pressure | Mpa | 7 | 8 | 9 | 10 | 11 | 11 | 10 | 9 | 8 | 7 | 7 | 8 | 9 | 10 | 11 | 11 | 10 | 9 | 8 | 7 | 7 | 8 | 9 | 10 | 11
| Net efficiency | % | 26.1567 | 25.6753 | 25.0618 | 24.3994 | 23.7259 | 26.4601 | 27.0572 | 27.6383 | 28.1677 | 28.5716 | 30.5928 | 30.2674 | 29.8075 | 29.2975 | 28.7711 | 30.7246 | 31.1887 | 31.6303 | 32.0222 | 32.2799 | 32.7302 | 32.4884 | 32.121 | 31.6951 | 31.2498
| Break-even price of electricity | EUR/MWh | 106.0066 | 107.5144 | 109.852 | 112.6397 | 115.7096 | 103.7167 | 101.5395 | 99.5738 | 97.9682 | 97.0168 | 90.5457 | 91.1067 | 92.2628 | 93.7124 | 95.3225 | 89.1779 | 87.9444 | 86.8629 | 86.0327 | 85.7296 | 84.5206 | 84.7668 | 85.5068 | 86.5125 | 87.6504
N2 | Live temperature | deg C | 500 | 500 | 500 | 500 | 500 | 550 | 550 | 550 | 550 | 550 | 600 | 600 | 600 | 600 | 600 | 650 | 650 | 650 | 650 | 650 | 665 | 665 | 665 | 665 | 665
| Live pressure | Mpa | 18 | 21 | 24 | 27 | 30 | 30 | 27 | 24 | 21 | 18 | 18 | 21 | 24 | 27 | 30 | 30 | 27 | 24 | 21 | 18 | 18 | 21 | 24 | 27 | 30
| Net efficiency | % | 24.1385 | 24.1517 | 23.9451 | 23.6455 | 23.3011 | 25.6349 | 25.9192 | 26.1576 | 26.2984 | 26.2246 | 27.9413 | 28.0719 | 27.9873 | 27.8012 | 27.5733 | 29.1735 | 29.3547 | 29.4845 | 29.5159 | 29.3417 | 29.7064 | 29.8973 | 29.8785 | 29.7604 | 29.596
| Break-even price of electricity | EUR/MWh | 114.4573 | 113.5502 | 114.0782 | 115.2695 | 116.8336 | 106.0204 | 104.9936 | 104.2783 | 104.1468 | 105.2401 | 98.6354 | 97.4134 | 97.2957 | 97.7102 | 98.3827 | 92.7942 | 92.3547 | 92.1773 | 92.4778 | 93.7687 | 92.5655 | 91.2441 | 90.9056 | 91.0376 | 91.4102
s-CO2 RC2E2/RC2E1 | Live temperature | deg C | 500 | 500 | 500 | 500 | 500 | 550 | 550 | 550 | 550 | 550 | 600 | 600 | 600 | 600 | 600 | 650 | 650 | 650 | 650 | 650 | 660 | 660 | 660 | 660 | 660
| Live pressure | Mpa | 18 | 21 | 24 | 27 | 30 | 30 | 27 | 24 | 21 | 18 | 18 | 21 | 24 | 27 | 30 | 30 | 27 | 24 | 21 | 18 | 18 | 21 | 24 | 27 | 30
| Net efficiency | % | 29.0938 | 30.1495 | 30.8164 | 31.2129 | 31.5087 | 32.9277 | 32.5939 | 32.1144 | 31.4193 | 30.3228 | 31.3157 | 32.4409 | 33.1942 | 33.6775 | 34.0561 | 34.9199 | 34.54 | 33.9936 | 33.2248 | 32.0881 | 32.2256 | 33.3807 | 34.1597 | 34.6764 | 35.09
| Break-even price of electricity | EUR/MWh | 92.998 | 90.044 | 88.4062 | 87.569 | 87.0328 | 83.0017 | 83.5909 | 84.5661 | 86.1508 | 88.9813 | 85.9008 | 83.1747 | 81.5474 | 80.6175 | 79.9626 | 77.6872 | 78.3215 | 79.3467 | 80.9374 | 83.5629 | 83.1523 | 80.5198 | 78.9084 | 77.9527 | 77.2551
Fig. 8.

## Delta T parametric study
Fig 8
RHX1 - cold end |  | K | 5 | 7.5 | 10 | 12.5 | 15
RHX2 cold end |  | K | [5 empty] | 5 | 7.5 | 10 | 12.5 | 15
RHX2 hot end |  | K | [10 empty] | 5 | 7.5 | 10 | 12.5 | 15
#REF! | s-CO2 RC2E2 | % | 35.0898 | 35.041 | 34.9644 | 34.8761 | 34.7755 | 34.9702 | 34.7726 | 34.5902 | 34.4074 | 34.2225 | 34.9648 | 34.6818 | 34.3179 | 33.8427 | 33.0406 | 0.31425
| Xenon | % | 31.4271 | 31.247 | 31.0708 | 30.8983 | 30.7489 | [10 empty] | 0.67814
| s-CO2 PE2 | % | 35.054 | 34.6849 | 34.3267 | 33.9766 | 33.6343 | [10 empty] | #REF!
| Helium | % | 29.8074 | 29.523 | 29.2432 | 28.968 | 28.6971 | [10 empty] | 1.1103
| Nitrogen | % | 28.0598 | 27.6261 | 27.2058 | 26.7972 | 26.4002
| s-CO2 RC2E2/RC2E1 | % | 32.2009 | 32.1786 | 32.1071 | 32.0745 | 31.9741 | 32.117 | 31.9621 | 31.8138 | 31.6678 | 31.5227 | 32.118 | 31.8721 | 31.5789 | 31.2122 | 30.6778
#REF! | s-CO2 RC2E2 | €/MWh | 78.2831 | 78.2556 | 78.3402 | 78.4767 | 78.66 | 78.3293 | 78.5573 | 78.839 | 79.1681 | 79.5285 | 78.3386 | 78.6423 | 79.2004 | 80.0505 | 81.6551
| Xenon | €/MWh | 84.5499 | 84.9192 | 85.3096 | 85.7103 | 86.0992
| s-CO2 PE2 | €/MWh | 76.4056 | 77.0252 | 77.6887 | 78.3712 | 79.0655
| Helium | €/MWh | 92.266 | 92.1093 | 92.3795 | 92.8424 | 93.4111
| Nitrogen | €/MWh | 97.6565 | 98.2716 | 99.1473 | 100.1679 | 101.2784
| s-CO2 RC2E2/RC2E1 | €/MWh | 83.824 | 83.8087 | 83.9469 | 84.0117 | 84.2522 | 83.9231 | 84.1169 | 84.3735 | 84.6666 | 84.9859 | 83.9208 | 84.2636 | 84.8109 | 85.5981 | 86.8631
-0.027579
Fig 12
|  |  | Case 1 | [9 empty] | Case 2 |  |  |  |  | Case 3
Fig 9
Fig 10

## Bottoming
He
| Live pressure | Mpa | 9 | 10 | 11 | 11.5 | 12 | 12.5 | 13 | 14
| Net efficiency | % | 32.7324 | 32.8496 | 32.9217 | 32.9409 | 32.9531 | 32.9582 | 32.9571 | 32.9396
| Break-even price of electricity | EUR/MWh | 83.4065 | 83.1757 | 83.0591 | 83.0426 | 83.0436 | 83.0627 | 83.0968 | 83.2024
N2
| Live pressure | Mpa | 15 | 18 | 21 | 24 | 27 | 30 | 33 | 36
| Net efficiency | % | 29.5973 | 30.0317 | 30.3451 | 30.5708 | 30.7376 | 30.86 | 30.9495 | 31.0133
| Break-even price of electricity | EUR/MWh | 91.7439 | 90.4525 | 89.572 | 88.9727 | 88.5573 | 88.277 | 88.0955 | 87.9902
s-CO2 RC2E2/RC2E1
| Live pressure | Mpa |  | 18 | 21 | 24 | 27 | 30
| Net efficiency | % |  | 35.3787 | 35.6703 | 35.887 | 36.05 | 36.1736
| Break-even price of electricity | EUR/MWh |  | 76.6453 | 76.1455 | 75.8075 | 75.583 | 75.4406
s-CO2 RC2E2/PE2
| Live pressure | Mpa | 28 | 31 | 34 | 37 | 40
| Net efficiency | % | 35.0123 | 35.0939 | 35.1587 | 35.21 | 35.2503
| Break-even price of electricity | EUR/MWh | 77.1736 | 77.0173 | 76.8964 | 76.8038 | 76.734
s-CO2 RC2E2/PE1
| Live pressure | Mpa | 28 | 31 | 34 | 37 | 40
| Net efficiency | % | 36.4177 | 36.5211 | 36.5914 | 36.6362 | 36.6613
| Break-even price of electricity | EUR/MWh | 75.1407 | 75.0177 | 74.9627 | 74.9601 | 74.998
Fig 8
RHX1 - cold end |  | K | 5 | 7.5 | 10 | 12.5 | 15
RHX1 - hot end |  | K | 30: 5; 33: 7.5; 36: 10 | 12.5 | 15
RHX2 cold end |  | K | [10 empty] | 5 | 7.5 | 10 | 12.5 | 15
RHX2 hot end |  | K | [15 empty] | 5 | 7.5 | 10 | 12.5 | 15
#REF! | Helium | % | 32.7307 | 32.7307 | 32.7307 | 32.7307 | 32.7307
| Nitrogen | % | 30.2509 | 30.2496 | 30.2484 | 30.2471 | 30.2458
| s-CO2 RC2E2/RC2E1 | % | 35.5804 | 35.5814 | 35.583 | 35.5849 | 35.5871 | [5 empty] | 35.583 | 35.5444 | 35.5083 | 35.4765 | 35.4436 | 35.5829 | 35.5908 | 35.5977 | 35.6102 | 35.6255
| s-CO2 RC2E2/PE2 | % | 35.0687 | 35.0682 | 35.0677 | 35.0673 | 35.0668 | 35.0687 | 35.0937 | 35.1181 | 35.1417 | 35.1646
| s-CO2 RC2E2/PE1 | % | 36.4907 | 36.4898 | 36.4889 | 36.4881 | 36.4872 | 36.4908 | 36.4887 | 36.4867 | 36.4845 | 36.4825
#REF! | Helium | €/MWh | 83.4114 | 83.2607 | 83.1819 | 83.1289 | 83.0971
| Nitrogen | €/MWh | 89.8316 | 89.7193 | 89.6464 | 89.5948 | 89.5564
| s-CO2 RC2E2/RC2E1 | €/MWh | 76.307 | 76.2969 | 76.2906 | 76.2861 | 76.2827 | [5 empty] | 76.2905 | 76.3312 | 76.3803 | 76.428 | 76.482 | 76.2907 | 76.2328 | 76.1892 | 76.1418 | 76.0911
| s-CO2 RC2E2/PE2 | €/MWh | 77.065 | 77.0158 | 76.9837 | 76.9606 | 76.943 | 77.065 | 76.9683 | 76.8891 | 76.8198 | 76.757
| s-CO2 RC2E2/PE1 | €/MWh | 75.0502 | 74.9905 | 74.9521 | 74.9243 | 74.9035 | 75.0501 | 74.9937 | 74.9577 | 74.9325 | 74.9136
|  |  | 15: 0; 30: 0 |  |  | 0 |  |  |  |  | 0
|  |  | 15: 0.0050921; 30: 0 |  |  | 0 |  |  |  |  | 0
|  |  | 15: -0.0067388; 30: 0 |  |  | 0.13939 |  |  |  |  | -0.042608
|  |  | 15: 0.0019731; 30: -0.095857 |  |  | 0 |  |  |  |  | 0
|  |  | 15: 0.003523; 30: 0.008272 |  |  | 0 |  |  |  |  | 0
|  |  | 15: 0.31427; 30: 0 |  |  | 0 |  |  |  |  | 0
|  |  | 15: 0.2752; 30: 0 |  |  | 0 |  |  |  |  | 0
|  |  | 15: 0.024264; 30: 0 |  |  | -0.19154 |  |  |  |  | 0.19964
|  |  | 15: 0.12205; 30: 0.30802 |  |  | 0 |  |  |  |  | 0
|  |  | 15: 0.14668; 30: 0.13652 |  |  | 0 |  |  |  |  | 0

## Carbon tax
Fig 13
CO2 cost |  |  | 0 | 25 | 50 | 75 | 100
#REF! |  | REF | 65.7576 | 68.3205 | 70.8835 | 73.4464 | 76.0094 | 10.2518 | 0.1559
#REF! | 2.1308 | s-CO2 RC2E2 | 78.3522 | 80.9018 | 83.4513 | 86.0008 | 88.5503 | 10.1981 | 0.13016
| 8.294 | Xenon | 84.5154 | 87.3497 | 90.184 | 93.0183 | 95.8526 | 11.3372 | 0.13414
|  | s-CO2 PE2 | 76.2215 | 78.7569 | 81.2924 | 83.8278 | 86.3632 | 10.1418 | 0.13306
|  | Helium | 92.2275 | 95.2157 | 98.2039 | 101.1921 | 104.1804 | 11.9529 | 0.1296
|  | Nitrogen | 97.6166 | 100.791 | 103.9654 | 107.1397 | 110.3141 | 12.6975 | 0.13008
|  | s-CO2 RC2E2/RC2E1 | 83.952 | 86.7282 | 89.5043 | 92.2805 | 95.0566 | 11.1046 | 0.13227
|  | s-CO2 RC2E2/PE2 | [5 empty] | 0 | #DIV/0!
|  | s-CO2 RC2E2/PE1 | [5 empty] | 0 | #DIV/0!
OPTIMAL |  | REF | 65.5195 | 68.0721 | 70.6247 | 73.1773 | 75.7299 | 10.2103 | 0.15584
| 11.5177 | s-CO2 RC2E2 | 71.1465 | 73.4348 | 75.723 | 78.0113 | 80.2996 | 9.1531 | 0.12865
|  | Xenon | 75.0328 | 77.5453 | 80.0578 | 82.5704 | 85.0829 | 10.0502 | 0.13394
|  | s-CO2 PE2 | 71.7361 | 74.117 | 76.498 | 78.8789 | 81.2598 | 9.5237 | 0.13276
|  | Helium | 82.8006 | 85.5064 | 88.2123 | 90.9181 | 93.624 | 10.8234 | 0.13072
|  | Nitrogen | 88.0696 | 90.9591 | 93.8486 | 96.7381 | 99.6275 | 11.5579 | 0.13124
|  | s-CO2 RC2E2/RC2E1 | 75.2155 | 77.6758 | 80.1362 | 82.5965 | 85.0569 | 9.8414 | 0.13084
|  | s-CO2 RC2E2/PE2 | 76.3806 | 78.9022 | 81.4238 | 83.9454 | 86.467 | 10.0864 | 0.13205
|  | s-CO2 RC2E2/PE1 | 74.7644 | 77.1995 | 79.6346 | 82.0697 | 84.5048 | 9.7404 | 0.13028
|  | REF | 59.6288 | 79.549 | 99.4693 | 119.3896 | 139.3098
11.5177
0.19316
| 5.9785 | 2.1308 | -12.5946 |  |  | 7.2057
|  | 8.294 | -18.7578 |  |  | 9.4827
|  |  | -10.4639 |  |  | 4.4853
-5.627
-9.5132
-6.2166
12.1074
Fig 13