## Sheet1
Recorded data and calculated parameters | [8 empty] | Pedigree criteria
Parameter | Reading interval | Reading error | Distribution | Mean | Standard deviation | Min | Max | CV | Factor / Score | 1 | 2 | 3 | 4 | 5
T1, HEx In (°C) | 0.1°C | - | Lognormal | 64.9839 | 1.0158 | 62.6 | 66.2 | 0.0157 | Measurement reliability (1) | Data is < 2 months old and/or recorded by fully calibrated sensor or fully qualified person | Data is < 6 months old and/or recorded by fully calibrated sensor or fully qualified person | Data is < 12 months old and/or recorded by fully qualified person | Data is > 12 months old and/or recorded by fully qualified person | Age or source of data unknown or > 12 months old
T2, HEx Out (°C) | 0.1°C | - | Lognormal | 27.4887 | 1.028 | 26 | 28.7 | 0.0276 | Basis of estimate (2) | Best possible data, use of historical field data, validated tools and independently verified data, given by fully qualified expert | Smaller sample of historic data, parametric estimates, internally verified data, some experience in the area | Limited available data, unverified, inexperienced opinions | Incomplete data, small sample, educated guesses, indirect approximate rule of thumb estimate | No experience in the data
T3, Temp dial out (°C) | 5.0°C | ±2.0°C | Normal | 35.8333 | 1.8645 | 32.5 | 37.5 | 0.0517 | Reading accuracy (3) | Measurements taken using fully calibrated and accurate equipment: ±0.1°C, ±0.1 bar | Measurements taken using recently calibrated but less accurate equipment: ±0.5°C, ±0.5 bar | Measurements taken using recently calibrated but less accurate equipment: >±1.0°C, >±1.0 bar | Measurements taken using accurate equipment that may need recalibrating | Measurements taken using un-calibrated and inaccurate equipment
T4, Temp blower (°C) | 2.0°C | ±0.5°C | Uniform | 18 | 0 | 18 | 18 | 0 | Environmental conditions (4) | Data recorded under specific consistent conditions or a specified range of conditions from area under study | Data recorded in generally consistent conditions with fluctuations specified | Data recorded in generally consistent conditions, changes not specified | Data recorded in a range of unspecified conditions | Data from unknown or distinctly different areas
P1, Pressure pre-HEx (bar) | 0.5 bar | ±1.0 bar | Normal | 1.7511 | 0.0765 | 1.6 | 1.8 | 0.0432 | Sample size (5) | > 20 | > 10 | > 5 | < 5 | Unknown
P2, Pressure post-HEx (bar) | 0.5 bar | ±0.3 bar | Uniform | 0.3 | 0 | 0.3 | 0.3 | 0
Pedigree matrix uncertainty indicators for all factors
Factor / score | 1 | 2 | 3 | 4 | 5
Measurement reliability (1) | 1 | 1.1 | 1.5 | 1.7 | 1.9
Basis of estimate (2) | 1 | 1.2 | 1.6 | 1.8 | 1.9
Reading accuracy (3) | 1 | 1.05 | 1.1 | 1.4 | 1.8
Environmental conditions (4) | 1 | 1.1 | 1.4 | 1.7 | 1.9
Sample size (5) | 1 | 1.2 | 1.4 | 1.6 | 1.9
Pedigree factors with relating GSD and CV
Factor | Dist. | Ped. score | Un. Ind. | GSD | CV
Measurement reliability (1) | Ln | 3 | 1.5 | 1.2247 | 0.2048
Basis of estimate (2) | Ln | 3 | 1.6 | 1.2649 | 0.2383
Reading accuracy (3) | Ln | 2 | 1.05 | 1.0247 | 0.0244
Environmental conditions (4) | Ln | 2 | 1.1 | 1.0488 | 0.0477
Sample size (5) | Ln | 3 | 1.4 | 1.1832 | 0.1694
CV aggregation results
PDF | CV comb. | CV agg. | CVT
Ln recorded | 0.0317 | 0.3701 | 0.3762
Ln pedigree | 0.3688
Norm. recorded | 0.0674 | 0.0676
Uni. recorded | 0