Figure 1. 	Inlet and outlet siloxane concentrations for one of the carbon contactors during a single exhaustion cycle (run time, 706 h between media changes).

Figure 2. Cumulative frequency curves developed using outlet siloxane data from GAC 1 to ascertain conformity to proposed warranty specification (Table 1). Data is provided from five consecutive exhaustion cycles.

Figure 3. Cumulative frequency curves developed ousing outlet siloxane data from all five GAC contactors to ascertain conformity to proposed warranty specifications (Table 1). Data is from a single exhaustion cycle in which all five contactors are assessed simultaneously.

Figure 4. Breakthrough curves for four of the GAC contactors which experienced breakthrough. Breakthrough is defined as the outlet concentration exceeding 30 mg m-3 for the third consecutive reading (equivalent to the Waukesha warranty limit, Table 1).

Figure 5. Media sampled at breakthrough, cross-sectioned (at centre) and analysed for Si to determine Si deposition in media operated at low Rep (GAC4, Re 30) and high Rep (GAC1, Re 81).

Figure 6. Evaluating the role of empty bed contact time (EBCT) in determining the number of bed volumes of biogas that can be treated before breakthrough. EBCT is determined by contactor length/superficial velocity.

Figure 7. Evaluating the role of the modified Reynold’s number (Rep) in determining the number of bed volumes of biogas that can be treated before breakthrough. The modified Rep was calculated based on specific contactor and media dimensions.

Table 1. Maximum silicon levels recommended by gas engine manufacturers

| Company | Jenbacher | Waukesha |
| --- | --- | --- |
| Silicon Specification† (mg/Nm3 CH4) | <20 | <50 |
| Silicon Specification†† mg/m3 biogas | <12 | <30 |

†as stated.  ††assume 60% CH4.

Table 2. Design parameters of contactors and media characterisation

|  |  | GAC1/2 | GAC3 | GAC4 |  | GAC5 |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Single | Pair | Single | Pair |
| Height | m | 1.90 | 2.00 | 1.60 | 3.21 | 1.85 | 3.70 |
| Diameter | m | 0.90 | 1.05 | 1.60 | 1.60 | 1.53 | 1.53 |
| Aspect ratio |  | 2.11 | 1.90 | 1.00 | 2.00 | 1.21 | 2.42 |
| Cross-sectional area | m | 0.64 | 0.87 | 2.01 | 2.01 | 1.83 | 1.83 |
| Volume | m3 | 1.21 | 1.73 | 3.22 | 6.44 | 3.38 | 6.76 |
| Inlet/outlet pipe diameter | m | 0.15 | 0.18 | 0.20 | 0.20 | 0.25 | 0.25 |
| Media mass | kg | 450 | 500 | 1000 | 2000 | 1500 | 3000 |
| BET surface area | m2 g-1 | 782.3430 |  |  |  |  |  |
| Total pore volume | cm3 g-1 | 0.13950 |  |  |  |  |  |
| Total pore area | m2 g-1 | 205.7447 |  |  |  |  |  |
| Average pore diameter | nm | 2.2022 |  |  |  |  |  |
| Particle diameter | mm | 4 |  |  |  |  |  |

Table 3. Operational conditions used in studies contactors (mean reported, n = 5-17)

| Contactor |  | GAC1 | GAC2 | GAC3 | GAC4 | GAC5 |
| --- | --- | --- | --- | --- | --- | --- |
| Media mass (kg) |  | 450 | 450 | 500 | 2000 | 3000 |
| Gas flowrate | (m3 h-1) | 323 | 258 | 396 | 408 | 1968 |
| Linear velocity | (m h-1) | 505 | 403 | 455 | 203 | 1075 |
| EBCT | (s) | 13.5 | 16.9 | 15.7 | 56.8 | 12.4 |
| Siloxane inlet concentration (mg m-3) | mean median max min | 77.3 64.5 313.8 22.9 | 77.3 64.5 313.8 22.9 | 77.3 64.5 313.8 22.9 | 77.3 64.5 313.8 22.9 | 77.3 64.5 313.8 22.9 |

Table 4. Estimate mass balance of GAC4 for fully speciated siloxanes and competing VOCs using a UKAS accredited GCMS trace analysis suite.

| Gas phase determinand | Inlet gas (mg m-3) | Outlet gas (mg m-3) | Total adsorbedb (g) |
| --- | --- | --- | --- |
| Siloxanes speciated |  |  |  |
| Hexamethylcyclotrisiloxane (D3) | <1.0 | <1.0 | N/a |
| Octamethylcyclotetrasiloxane (D4) | 3.1 | 2.8 | 66.8 |
| Decamethylcyclopentasiloxane (D5) | 33.9 | 7.2 | 5947.2 |
| Dodecamethylcyclohexasiloxane (D6) | <1.0 | <1.0 | N/a |
| Hexamethyldisiloxane (L2) | <1.0 | <1.0 | N/a |
| Octamethyltrisiloxane (L3) | <1.0 | <1.0 | N/a |
| Decamethyltetrasiloxane (L4) | <1.0 | <1.0 | N/a |
| Dodecamethylpentasiloxane (L5) | <1.0 | <1.0 | N/a |
| Trimethyl Silanol (toluene equivalent) | <1.0 | <1.0 | N/a |
| Non-siloxane species detected |  |  |  |
| Total Organo-Sulphur Compounds as S | 1.5 | N/d | 334.1 |
| Nonane | 15.7 | <5.3 | 2316.5 |
| Decane | 52.4 | <5.8 | 10379.7 |
| Cumene | 1.5 | <1.0 | 111.4 |
| d-Limonene | 4.5 | 2.4 | 467.8 |
| alpha-Pinene | 3.1 | 1.3 | 400.9 |
| beta-Pinene | 1.8 | <1.0 | 178.2 |
| Toluene | 12.6 | 1.7 | 2427.9 |
| Ethyl benzene | 10.4 | 5.3 | 1136.0 |
| m,p-Xylene | 32.2 | 18.8 | 2984.7 |
| o-Xylene | 11.9 | 6.8 | 1136.0 |
| o-ethyltoluene | 2.1 | 1.9 | 445.5 |
| 1,2,3 – Trimethylbenzene | 4.4 | 1.5 | 646.0 |
| 1,2,4 – Trimethylbenzene | 13.2 | 8.6 | 1024.6 |
| 1,3,5 – Trimethylbenzene | 4.5 | 4.3 | 445.5 |
| Total cyclic siloxane mass adsorbed |  |  | 6014 |
| Specific cyclic siloxane mass adsorbed (g kg-1) |  |  | 3 |
| Mean specific siloxane breakthrougha |  |  | 8 |
| Total mass adsorbed |  |  | 30448 |
| Specific total mass adsorbed (g kg-1) |  |  | 15 |

aBased on real-time mass balance (from Table 4). bProvides an estimate based on mass balance of GAC4 to average breakthrough (34587 Bv).

Table 5. Estimation of full scale carbon vessel operation from the literature compared to this study.

|  |  | This study (GAC1) | Tower & Wetzel, 2004e | Orange County Sanitation District | Liang et al., 2001 | Wheless & Pierce, 2004 / Wheless & Gary, 2002 |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | Carbon | SAGTM (graphite based) | SAGTM (graphite based) | Carbon and graphite | Carbon and graphite |
| Volume | m3 | 1.21 | 26.6 | 10.0 | 0.2 | 0.07 |
| Pressure | bar | 0.12 | N/s | 4.0 | 4-4.4 | N/s |
| Gas flow | m3 h-1 | 323 | 1700-2800 | 2450 | 177 | 85 |
| EBCT | s | 12.8 | 34-56 | 14.7 | 4.7 | 2.9 |
| Inlet concentration | mg m-3 | 65.4a | 0.58-1b, 4.5-13.0c | 76 | 38-62 | N/s |
| Siloxane loading | mg kg-1 h-1 | 46.9 | 3.34 | 41.2 | 88.9 | N/s |
| Specific media capacity | g kg-1 (%w/w) | 21.5 (2.1) | 7.2 (0.72)d | 75.0 (7.5) | 59.5 (5.95) | 10-15 (1.0-1.5) |
| Time to breakthrough | d | 16.4 | ~90 | 77 | 21-28 | nd |
| Sampling method | - | Online | Impinger (MeOH) | Bag/ Canister | Impingerf | ns |
| Analytical method (Speciation)/ Limit of detection | - mg m-3 | FTIR (Cyclic/linear) 7 | GC-MS (Speciation) 0.3 L2, 0.29 D6 | GC-MS (Total) N/s | HPLCf (Total VMS) N/s | nd |
| Outlet concentration | mg m-3 | 7.0 | N/d | Bdl | Bdl | N/d |

N/s – Not stated. N/d – None detected. Bdl – Below detection limit. aPrincipally loaded with D5; GAC1. bmgD5 m-3. cmgD4 m-3. dAssumes 100% retention at maximum flow. eAs cited in Soreanu et al. (2011). fVariation of USEPA method TO-5.